3-PART CSI MASTERFORMAT SPECIFICATION

SECTION 079513

EXPANSION JOINT COVER ASSEMBLIES

PART 1 - GENERAL

1.01	Work Included

A.	The work shall consist of furnishing and installing fire barrier assemblies in accordance with the details shown on the plans and the requirements of the specifications.  The fire barrier assemblies are proprietary designs utilizing pre-engineered components and materials tested to meet a required fire endurance rating expressed in hours.

B.	Related Work

- Cast-in-place concrete

- Miscellaneous and ornamental metals

- Flashing and sheet metal

- Sealants and caulking

1.02	Submittals

- Template Drawings - Submit typical fire barrier cross-section(s) indicating pertinent dimensioning, general construction, and relationship to expansion control system (if applicable).

- Test Reports - Submit nationally recognized independent third-party test report or engineering evaluation certifying product to meet the required test standard(s) and fire endurance rating.

1.03	Product Delivery, Storage and Handling

- Deliver products in manufacturer's original carton or labeled containers and store under cover in a dry location until installed. Store off the ground, protect from weather and construction activities.

1.04	Acceptable Manufacturer

- Subject to compliance with requirements, provide products from the following:

Nystrom

9300 73rd Avenue North
Minneapolis, MN 55428
PH: (800) 547-2635
www.Nystrom.com

- Alternate manufacturers and their products will be considered, provided they meet the required fire rating, and are produced of materials that are equal to or superior to those used in the specified fire barrier assembly.

- Any proposed alternate systems must be submitted and receive approval 21 days prior to the bid.  All post bid submittals will not be considered.  This submission shall be in accordance with MATERIALS AND SUBSTITUTIONS.

Any manufacturer wishing to submit for prior approval must provide the following:

- A working 6 inch sample of the proposed system with a letter describing how system is considered superior to the specified fire barrier assembly.

- A project proposal drawing that illustrates the recommended alternate system installed in the construction that is specific to the project.  Typical catalog cut sections will not be considered.

- Nationally recognized third-party test report certifying that proposed system meets all required test standards and fire endurance ratings.

Incomplete test reports or letters submitted from the manufacturer substituting as third-party certification will not be permitted.

- Verifiable list of prior installations showing prior and successful experience with the proposed systems.

- Any substitution products not adhering to all specification requirements within, will not be considered.

PART 2 - PRODUCT

2.01	General

A.	Provide encapsulated fire barrier assembly that has been designed to provide the required fire endurance rating, minimize passage of smoke and accommodate moderate movement without stress or degradation to its components.  System components and their splices shall be installed without adhesives, caulks or sealants.  Documentation by a recognized third-party witnessing agency shall certify that the system has been tested and meets the requirements of ASTM E-119, NFPA 251, UBC 7-1 and CAN/ULC - S101 for fire endurance.

Furnish Fire Barrier System for rated openings up to and including 3 inches as provided by Nystrom and as indicated on drawings.

2.02	Components and Materials

A.	Fire Blanket - Provide high purity ceramic fiber blanket encapsulated in a fiberglass reinforced aluminum foil to minimize dusting and passage of smoke.  The blanket shall meet the following requirements:

Physical Properties				Values

Density						8 PCF

Melting Point					3200 degrees Fahrenheit

Service Limit					2300 degrees Fahrenheit

Flame Spread (ASTM E-84)			0

Smoke Developed (ASTM E-84)			0

Color						White

B.	Encapsulation Envelope (Smoke Barrier) - Provide fiberglass reinforced aluminum foil meeting the following requirements:

Physical Properties	Test Method	Values

Thickness	      ----	8 mils

Tensile Strength	ASTM C-1136	45 lbs/inch width (MD)

45 lbs/in width (XD)

Reinforcing 	      ----	4/inch (MD)

(Bi-directional fiberglass)		4/inch (XD)

Puncture Resistance	ASTM C-1136	130 Beach units

Bursting Strength	ASTM D-774	90 psi

Flame Spread	ASTM E-84	5

Smoke Developed	ASTM E-84	10

C.	Fire Tape - Provide .045 inch by 2 inch wide durable woven textile meeting the following requirements:

Physical Properties				Suggested Requirements

Tensile Strength					6,000 lbs.(min.)

Elongation @ 2500lbs				20% (max.)

Breaking Strength (after bar abrasion)		4800 lbs. (min.)

Flammability					Self-extinguishing

D.	Accessories - Provide necessary and related parts required for complete installation.

2.03	Fabrication

- Fire barrier blankets shall be shipped in standard individual rolls 25 feet in length.

- Fire Tape and hardware required for a complete installation will be shipped as loose components in manufacturer’s standard shipping carton.

- Fire Barrier Blankets shall be cut in the field for exact length and changes in direction.

PART 3 - EXECUTION

3.01	Installation

A.	Protect all fire barrier components from damage during storage, installation and post installation activities including placement of expansion control system.

B.	Fire barrier assembly shall be installed in strict accordance with manufacturer’s installation procedures along with the advice of their product engineers.

C.	Fire barrier assembly shall be installed in the correct width of opening as called for in the contract plans.  Variations in width shall be brought to the attention of the architect and product manufacturer prior to the installation of any material.

3.02	Clean and Inspect

A.	Upon completing installation of the Fire Barrier Assembly, inspect all splices for proper installation.  Clean and remove any debris that is observed resting on the exposed top surface of the fire barrier blankets.

END OF SECTION

REV 03/20